## ELECTRICAL ESTIMATION
ELECTRIFICATION WORK
Sl. No. | Specification of work | Unit | Measurements |  |  |  | Qty. | Basic Rate | 5% Area Wt | Amount
|  |  | No | L | B | H/D
1 | Concealed Conduit System : Supplying heavy gauge PVC conduit pipe ...... mm dia..........mm thick confirming to IS 2509 with suitable size bends, metal/PVC Junction boxes, adhesive paste etc., and running before concreting the slab. The conduit should be tied to the reinforcement rods by using binding wires and unused ways of junction boxes and pipe ends should be covered using PVC end enclosures, run with 18SWG GI fish wire wherever necessary PWD Ele. SR 2023-24, Pg. No. 2, It No. 1.2.1
| 19/20 mm dia 2 mm thick | Rmt |  |  |  |  | 60.0091
60.0091
| Basic Rate |  | Rs | 66
2 | Supplying heavy gauge PVC Conduit Pipe .... dia ....... mm thick with suitable size bends, metal junction boxes adhesive paste etc., by groove cutting in the wall and fixing by bracing U or J hooks and cement plastering upto the wall surface and run with 18 SWG GI fish wire run throughout the conduit wherever necessary.PWD Ele. SR 2023-24, Pg. No. 2, It No. 1.3.1
| 19/20 mm dia 2 mm thick | [5 empty] | 30.4878
|  | Rmt |  |  |  |  | 30.4878
| Basic Rate |  | Rs | 68
3 | Wiring for lighting/power circuit using one of FRLS PVC insulated 1100V grade, multistrand copper wire with low conductor resistance single core in open or concealed system of wiring with specified IS 694:confirming to latest amendments.PWD Ele. SR 2023-24, Pg. No. 6, It No. 2.3.3
| 2.5 Sqmm | Mtr |  |  |  |  | 3000
3000
| Basic Rate |  | Rs | 42
4 | Wiring for lighting/power circuit using one of FRLS PVC insulated 1100V grade, multistrand copper wire with low conductor resistance single core in open or concealed system of wiring with specified IS-694:confirming to latest amendments.PWD Ele. SR 2023-24, Pg. No. 6, It No. 2.3.4
| 4 Sqmm | Mtr |  |  |  |  | 3000
3000
| Basic Rate |  | Rs | 63
5 | Supplying and fixing PVC/metal conduit Deep junction box,PWD Ele. SR 2023-24, Pg. No.2,
| PVC JUNCTION BOX 25 mm deep Junction box | Nos | 45 |  |  |  | 45
| Basic Rate |  | Rs | 45 |  |  | 45
6 | ExtraforGroovecuttinginbrickwall/CCfloor tothesuitabledepth for concealing of Conduit/GI pipe and plastering, finishing uptowall surface complete.PWD Ele. SR 2023-24, Pg. No.2, ITEM NO:1.7.1
| Groove Cutting up to 50mm | MTR | 50 |  |  |  | 50
| Basic Rate |  | Rs | 29 |  |  | 50
7 | Supplying And Fixing Metal Fan Box with Round Hook.
| FAN JUNCTION BOX | NO | 8 |  |  |  | 8
| Basic Rate |  | Rs | 117 |  |  | 8
8 | Supplying and flush mounting powder coated / galvanized metal box suitable for mounting modular switch plates. The box should be firmly flush mounted after due groove cutting in Brick/Stone/C.C wall PWD Ele. SR 2023-24, Pg. No. 9, It No. 3.4.3
| 4-5 way | Nos |  |  |  |  | 3
3
| Basic Rate |  | Rs | 177
| 8 way | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 261
| 10-12 way | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 319
9 | Supplying and fixing superior quality modular switch mounting polycarbonate plate with necessary supporting back plate with required nos. of machine screws, bolts nuts etc., complete on the existing metal/PVC box.PWD Ele. SR 2023-24, Pg. No. 9, It No. 3.5.3
| 4 Module | Nos |  |  |  |  | 3
3
| Basic Rate |  | Rs | 175
| 8 Module | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 284
| 12Module | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 344
10 | Supplying and fixing of modular switch & connected accessories on existing modular switch plate as per IS 3854 and IS 1293.PWD Ele. SR 2023-24, Pg. No. 10, It No. 3.6.1
| 6A One Way Switch | [5 empty] | 2
|  | Nos |  |  |  |  | 2
| Basic Rate |  | Rs | 102
11 | Supplying and fixing of modular switch & connected accessories on existing modular switch plate as per IS 3854 and IS 1293.
PWD Ele. SR 2023-24, Pg. No. 10, It No. 3.6.3
| 6A Three Way socket | [5 empty] | 8
|  | Nos |  |  |  |  | 8
| Basic Rate |  | Rs | 171
12 | Supplying and fixing of modular switch & connected accessories on existing modular switch plate as per IS 3854 and IS 1293.PWD Ele. SR 2023-24, Pg. No. 10, It No. 3.6.4
| Stepped Regulator | [5 empty] | 20
|  | Nos |  |  |  |  | 20
| Basic Rate |  | Rs | 357
13 | Supplying and fixing of modular switch & connected accessories on existing modular switch plate as per IS 3854 and IS 1293.PWD Ele. SR 2023-24, Pg. No. 10, It No. 3.6.10
| 6/16A Universal Socket | [5 empty] | 4
|  | Nos |  |  |  |  | 4
| Basic Rate |  | Rs | 236
14 | Supplying & fixing miniature circuit breakers on existing MCB distribution boards using necessary fixing materials and 'C' Type curve, indicator ON/OFF, energy cross-3 with Short circuit breaking capacity of 10K and complete wiring as required confirming to IEC 60898.PWD Ele. SR 2023-24, Pg. No. 27, It No. 5.18.1
| 6-32 A SP | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 415
15 | Supplying and fixing regular MCB distribution boards on wall/ood board / flush mounting using required clA, bolts, nuts etc., with provision for fixing suitable type capacity MCB's single phase/3 phase/single door with powder coated painting Made out of 14 SWG MS enclosure.PWD Ele. SR 2023-24, Pg. No. 28, It No. 5.19.2
| 6 Way SP & N | Nos |  |  |  |  | 2
2
| Basic Rate |  | Rs | 1186
16 | Supplying and fixing angle iron frame work fabricated out of M.S. angle iron.. and M.S. Flat......with bolts, washers etc., and painted with 2 coats of red oxide and then two coats of approved paint.PWD Ele. SR 2023-24, Pg. No. 30, It No. 5.41.2
| 50 x 50 x 6 mm | Nos |  |  |  |  | 5
5
| Basic Rate |  | Rs | 395
17 | Supplying of 1.1 Kv LT UG cable XLPE or heat resistance PVC Insulated PVC Extruded inner sheath armoured UG LT csble as per IS-1554( part-1) PWD Ele. SR 2023-24, Pg. No. 40, It No. 32.05
| 4 core 16Sqmm | Mtr |  |  |  |  | 100
100
| Basic Rate |  | Rs | 141.842
18 | Supplying capacitor type ceiling fan complete with down rod blades, shackle, canopies etc, for operation on 230 V, 50 cycles. Single phase AC supply conforming to ISS-374- 1979 and with double ball bearing system.48" Sweep (1200 mm) Regular model PWD Ele. SR 2023-24, Pg. No. 46, It No. 6.3
|  | Nos |  |  |  |  | 8
8
| Basic Rate |  | Rs | 2984
19 | Fixing a ceiling /wall mounting fan of all capacities and all types, with necessary clA and 'S' hook made out of 15mm dia MS rod, with 5 A. ceiling rose of approved quality with necessary length of 23/0.0076 inch PVC insulated twin twisted wire of approved quality, mounted on a suitable size wooden board and wired.PWD Ele. SR 2023-24, Pg. No. 80, It No. 13.10
|  | Nos |  |  |  |  | 8
8
| Basic Rate |  | Rs | 171
20 | Supplying of .....feet -PVC Batten with integrated LED tube .... W with high quality diffuser with Life of 25000 burning hours & 70% lumen maintenance with CRI > 80. Power Input: 220-240V@ 50/60Hz & Power factor >0.9 along with CE approved. 2 years Warranty against any manufacturing defect working under standard electrical condition PWD Ele. SR 2023-24, Pg. No. 64, It No. 11.3.2
|  | Nos |  |  |  |  | 5
5
| Basic Rate |  | Rs | 690
21 | Supplying&fixingretrofittype-PL-LEDLamp......WLEDlinearsourcewithCCT6500degreeK,CRI>70%.efficacy>80lumenperW,life>25000burninghoursandCompliancetoIS10322/IEC60598,LM79&LM80.TheLEDaredrivenbyHFelectronicdriverintegratedinthesystem,withPF>0.95,powerlossshould<5%oflampWage.,shortcircuit&opencircuitprotectiontobeintegratedinthecircuit,THDlessthan20%,LifeasperLM79.Theoperatinginputvoltageshouldbebetween130to275V.TestedbyNABL/CPRIaccreditedlaboratorywith2yearsWarrantyagainstany manufacturing defect working under standard electrical condition.PWD Ele. SR 2023-24, Pg. No. 43, It No. 11.2.2
| 18-20wa | Nos |  |  |  |  | 3
3
| Basic Rate |  | Rs | 702
22 | Supplying of .. TR Invertor type split Air conditioners suitable foroperation on A/C supply single phase 50 Hz 230 V with hermetically sealed inverter compressor with air cooled condenser, latest R410A / R-32 refrigerant fan motor, start & run capacitors, relay & over load protector internal unit, with one indoor & one outdoor unit The condenser unit will be placed outside the room avoid noise including standard length of suitable size copper tubing covered with nitrile rubber insulation tube. suitable capacity 3 core sheathed/ PVC copper cable and a battery operated wireless remote unit. PWD Ele. SR 2023-24, Pg. No. 31, It No. 6.8.2
| 1.5 Ton capacity 3 Star | 5 |  |  |  | nos | 5
23 | Smart Surveillance System (CCTV): using PTZ & Fixed cameras, OFC monitoring system, HMI etc., as per specificationPWD Ele. SR 2023-24, Pg. No. 31, It No. 8525
PTZ Camera Specification: • Lens type: Auto focus with Optical Zoom of 30x, Digital Zoom +10x • Pan Angle: 360 degree endless • Tilt Angle: 210 degree with e-flip or higher • Zoom : 30x Optical and 12x Digital • Mode :Day and Night • Image size: Full HD • Streaming: High speed • Weather Proof: IP 66 compliant • Network Protocol: TCP/IP should be compliant of any other protocol required. • Connectivity : Cat 6 / Optical fibre • Ethernet: 10Base-T/100Base-TX(RJ45) • Power source : both self powered and externally powered
[6 empty] | nos | 6
Total Rs.
Say