AIR CONDITIONING

DESIGN BASIS REPORT

AIR CONDITIONING FOR OFFICE BUILDING,

BASIS OF DESIGN FOR NEW AIR CONDITIONING SYSTEM

# CODES AND STANDARDS:

Apart from the specific equipment standards and specifications, the following broad certifying agency / standards have been considered while designing the system in accordance with the Thermodynamic Principles.

- ASHRAE Standards

- ASHRAE                       :		90.1 – Energy Standard for Buildings Except 							Low – Rise Residential Buildings

- ISHRAE		   :		Weather Data

- ARI			   :		Cooling Coil ratings

# DESIGN PARAMETERS

OUTDOOR DESIGN DATA:

CITY NAME ……………                                         BANGALORE

LOCATION 	…………………………………….	INDIA

LATITUDE 	…………………………………….	12.58° N.

ELEVATION ………………………………………       	3020 FT

SUMMER DESIGN DRY-BULB…………………   	96.0°F

SUMMER COINCIDENT WET-BULB…………… 	78.0°F

RELATIVE HUMIDITY ……………………………	45.0 %

SUMMER DAILY RANGE………………………… 	22.0 °F

MONSOON DESIGN DRY-BULB…………………  	82.0 °F

MONSOON COINCIDENT WET-BULB…………… 	78.0 °F

RELATIVE HUMIDITY ………………………………	82.0 %

WINTER DESIGN DRY-BULB………………………   	58.0 °F

WINTER DESIGN WET-BULB………………………   	54.0 °F

RELATIVE HUMIDITY ………………………………	78.0 %

## INSIDE DESIGN CONDITIONS:

The Indoor Temperature to be maintained is as follows:

TEMPERATURE                        	:           72ºF ± 1.8 ºF (22 ºC ± 1ºC)

RELATIVE HUMIDITY		:	55+/-5 % considered only for

Calculation Purpose (* Variable)

# ESTIMATed COOLING LOAD:

Cooling load is about 54.5TR as assessed using computer programme based on ASHRAE / ISHRAE methodology.

# proposed air conditioning SYSTEM DESCRIPTION

## RECOMMENDATION: It is recommended to install multiple units of DUCTABLE Type Air conditioning System, CASSETTE TYPE & HI WALL TYPE SPLIT AIR CONDITIONER SYSTEMS.

The air conditioning system shall comprise of Air-cooled Condensers Having Scroll type Compressors condensing unit The Refrigerant used will be R22

.

CASETTE TYPE INDOOR UNIT

HI WALL TYPE SPLIT AIR CONDITIONER

DUCTABLE TYPE SPLIT AIR CONDITIONER